## Summary
SA Energy Transformation RIT-T Project Assessment Conclusions Report (PACR)
Market Modelling and Assumptions Databook
Summary | Description
ISP Projects | ISP Projects added to the model and commissioning years
Transmission build limits | Potential in each Renewable Energy Zone (REZ) to build new renewables
Cycling of thermal plant | Minimum operating and down times for thermal generators
Inertia | Calculated inertia of South Australian generators and additional plant
DSP | Lists assumed demand side participation
Battery aggregation | Aggregation of household battery installations by NEM region
Build cost | Build costs for new entrant generator classes
Connection cost | Cost to connect different generation classes according to REZ and region
Maximum capacity | Installed capacity of existing and committed generators. Existing generators refer to maximum seasonal ratings.
Generation limits | Generator minimum load, minimum and maximum capacity factors
Minimum Reserve Levels | Minimum reserve levels used in capacity expansion modelling
Interconnector Firm Capacity | Lists NEM interconnector firm capacity
QRET | Queensland Renewable Energy Target - 50% by 2030
VRET | Victorian Renewable Energy Target - 40% by 2025
Emission Trajectory | NEM emissions targets
Interconnector Capability | Lists interconnector capability between NEM regions
QNI Augmentations | Lists augmentations to QNI and the effect on QNI capability
Storage properties | Storage to power ratio, lifetime and round-trip efficiency
Coal and Biomass price | Fuel price for each coal and biomass generator
Gas and liquid fuel price | Fuel price for each gas and liquid fuel generator
Refurbishment | Generator refurbishment costs, dates and supporting parameters
Retirement | Generator end of technical life and retirement costs
Heat rates | Generator heat rates
Auxiliary | Generator auxiliary loads
Fixed OPEX | Fixed operating and maintenance cost
Variable OPEX | Variable operating and maintenance cost
Emissions | Generator emission rates
Inflation | Forecast price inflation
Rooftop PV | Forecast rooftop solar PV by NEM region

## ISP Projects
ISP Projects
Name | ISP Status | Network augmentation | Thermal rating | R | X | Notional Improvement (MW) | Estimated cost ($M) | Timing | Reason for inclusion
ISP Project - QNI Option 3 | Group 1 | Uprate Liddell-Muswellbrook-Tamworth and Liddell-Tamworth 330 kV lines | 1160 MVA |  |  | +460/-190 | 142 | 2023
|  | SVCs at Dumaresq and Tamworth substations and, shunt cap banks at Tamworth, Armidale and Dumaresq | Updated notional constraint across QNI - see notional improvement
ISP Project - VNI Option 1 | Group 1 | Uprate the Upper Tumut-Canberra 330 kV line | 1115 MVA |  |  | 120 | 5 | 2020 | Aleviate constraints along the path of the preferred option. The PADR tested the benefits of not undertaking this augmentation
|  | Install second 500/330 kV 1000 MVA transformer at South Morang. | 1000 MVA | 0.00016 pu | 0.01185 pu
|  | Uprate Dederang-South Morang 330 kV lines and series capacitors. | 1108 MVA |  |  | 170
ISP Project - Vic Renewable Integration RIT-T | Group 1 | 2x500 kV new circuits between Ballarat and Sydenham 2x500/220 kV transformers at Ballarat | 2500 MVA 1000 MVA | 0.0005 pu 0.000147 pu | 0.0077 pu 0.01789 pu |  |  | 2025 | Inclusion will reduce the cost of option(s) D
|  | 2x220 kV new circuits between Ararat and Ballarat | 800 MVA | 0.0062 pu | 0.0664 pu |  | 146 | 2024
ISP Project - QNI Option 5 | Group 2 | 2x330 kV new circuits between Armidale and Bulli Creek: Armidale-Dumaresq Dumaresq-Bulli Creek | 1143 MVA 1445 MVA | 0.00376 pu 0.00384 pu | 0.04763 pu 0.04518 pu | +460/-568 | 525 | 2025
ISP Project - QNI Option 5 (delayed) | Group 2 | 2x330 kV new circuits between Armidale and Bulli Creek | 1143 MVA 1445 MVA | 0.00376 pu 0.00384 pu | 0.04754 pu 0.04518 pu | +460/-568 | 525 | 2035 | SA to Queensland interconnector may influence the timing of these developments. These properties test a delay to 2035 (ten years)

## Transmission build limits
Transmission build limits (MW)
Potential in each zone to build new renewable energy capacity
This will be moderated by transmission expansion choices in each scenario, loss factor impacts, etc
REZ Number | Renewable Energy Zone | Region | Wind |  | Solar | Transmission-limited total build | Solar and storage coupling | Indicative transmission expansion cost ($M/MW) | Estimated annuity payment ($Annual/MW)
|  |  | High | Medium |  |  |  |  | 6% WACC 50 yr life | Option A | Option B | Option C3 | Option C3ii - alternative path | Option Ciii - HVDC | Option D | Comments
0 | Far North QLD | QLD |  |  | 0 | 700 |  | 1.1927 | 75670.5669
1 | North QLD Clean Energy Hub | QLD | 2320 | 6955 | 4000 | 0 |  | 1.2878 | 81702.2788
2 | Northern QLD | QLD |  |  | 1750 | 2500 |  | 0.89885 | 57027.0939
3 | Barcaldine | QLD | 475 | 1435 | 4000 | 0 |  | 0.96306 | 61100.4578
4 | Isaac | QLD | 465 | 1395 | 3500 | 2800 |  | 0.69143 | 43866.9953
5 | Fitzroy | QLD | 220 | 670 | 2000 | 3000 |  | 0.51857 | 32900.2465
6 | Darling Downs | QLD | 695 | 2090 | 4000 | 3000 |  | 0.17286 | 10966.7488
7 | North West New South Wales | NSW |  |  | 3250 | 100 |  | 0.29558 | 18753.1405
8 | Northern NSW Tablelands | NSW | 900 | 2760 | 1750 | 300 |  | 0.29558 | 18753.1405
9 | Central NSW Tablelands | NSW | 400 | 1200 | 3000 | 1000 |  | 0.29558 | 18753.1405
10 | Central West NSW | NSW | 355 | 1065 | 3750 | 100 |  | 0.29558 | 18753.1405
11 | Southern NSW Tablelands | NSW | 575 | 1735 | 0 | 1000 |  | 0.23232 | 14739.3104
31 | Tumut | NSW |  |  | 0 | 0 |  | 0.23232 | 14739.3104
13 | Murray River (NSW) | NSW | 1055 | 3140 | 6000 | 0 |  | Note 4 |  |  |  | +800 [Note 1] | +400 [Note 2] | +800 [Note 3] |  | Note 1: Additional 800 MW to option C3 delivered by Buronga - Darlington Point - Wagga. Note 2: Additional 400 MW to Option C3ii devilered by Dalington Point - Wagga Note 3: Additonal 800 MW from mid-point terminal. Note 4: Model driven augmentation not considered. Augmentation explicitly included as part of the options considered.
13 | Murray River (VIC) | VIC |  |  |  | 100 [Note 1] |  | 0.38996 | 24740.9854 |  |  | +400 [Note 2] | +800 [Note 3] | +400 [Note 4] |  | Note 1: Updated to reflect committed generators. Note 2: Additional 400 MW to option C3. Note 3: Additional 800 MW to option C3 ii. Note 4: Additional 400 MW to option C3 iii.
18 | Riverland (NSW) | NSW | 155 | 465 | 2000 | 200 |  | Note 1 | [7 empty] | Note 1: Model driven augmentation not considered. Augmentation explicitly included as part of the options considered.
18 | Riverland (SA) | SA |  |  |  | 250 |  | Note 1 | [7 empty] | Note 1: Model driven augmentation not considered. Augmentation explicitly included as part of the options considered.
12 | Broken Hill | NSW | 620 | 1870 | 4000 | 100 |  | Note 2 |  |  | +700 [Note 1] |  |  |  |  | Note 1: REZ capability increased with the inclusion of mid-point terminal station. Note 2: Model driven augmentation not considered. Augmentation explicitly included as part of the options considered.
30 | New England | NSW |  |  | 0 | 300 |  | 0.29558 | 18753.1405
32 | Cooma-Monaro | NSW |  |  | 0 | 200 |  | 0.23232 | 14739.3104
14 | Western Victoria | VIC | 395 | 1185 | 0 | 2000 [Note 1] |  | Note 3 | [5 empty] | Note 2 |  | Note 1: Western Victoria RIT-T assumed in the base case. Timing is to match the development of Option D. Note 2: Increasing connection between Tungkillo and Horsham in addition to the Western Victoria RIT-T augmentations does not increase access to the Western Victoria REZ. Note 3: Model driven augmentation not considered. Augmentation explicitly included as part of the options considered.
15 | Moyne | VIC | 570 | 1725 | 0 | 2000 |  | 0.088883 | 5639.1022
16 | Gippsland | VIC | 35 | 105 | 0 | 2000 |  | 0 | 0
33 | Ovens Murray | VIC |  |  | 0 | 300 |  | 0 | 0
17 | South East SA | SA | 455 | 1355 | 0 | 500 |  | 0.25928 | 16450.1232
19 | Mid-North SA | SA | 605 | 1820 | 0 | 1000 |  | 0.25928 | 16450.1232
20 | Yorke Peninsula | SA | 155 | 465 | 0 | 50 |  | 0.12964 | 8225.0616
21 | Northern SA | SA |  |  | 1500 | 1000 | Yes | 0.25928 | 16450.1232
22 | Leigh Creek | SA | 295 | 895 | 3250 | 0 [Note 1] | Yes | 0.51857 | 32900.2465 | [6 empty] | Note 1: Leigh Creek transmission capability set to zero from 10. Whilst 10 MW could be accomodated, transmission losses and the absence of scale efficiencies are unlikely to see this capability utilised.
23 | Roxby Downs | SA |  |  | 1700 | 960 | Yes | 0.30413 | 19295.55
24 | Eastern Eyre Peninsula | SA | 290 | 870 | 2500 | 500 | Yes | 0.38893 | 24675.1849
25 | Western Eyre Peninsula | SA | 175 | 540 | 2000 | 0 | Yes | 0.38893 | 24675.1849
26 | King Island | TAS | 150 | 450 | 0 | 0 |  | 1.21 | 76767.2418
27 | North East Tasmania | TAS | 75 | 230 | 0 | 0 |  | 0.1257 | 7975.0197
28 | North West Tasmania | TAS | 500 | 1500 | 0 | 200 |  | 0.23253 | 14752.4705
29 | Tasmania Midlands | TAS | 430 | 1300 | 0 | 1000 |  | 0.0726 | 4606.0345
PACR 1 | Eastern and Western Eyre Peninsula (Eyre Peninsula) | SA |  |  |  | 500 |  | 0.38893 | 24675.1849 | [6 empty] | Cost to expand the Eyre Peninsula enables capacity in Western Eyre Peninsula, Eastern Eyre Peninsula or both.
PACR 2 | Mid-North and Northern SA (Northern Hub) | SA |  |  |  | 1000 |  | 0.25928 | 16450.1232 | [6 empty] | Cost to expand Northern SA includes cost to expand Mid-North SA
PACR 3 | Northern Hub and Leigh Creek | SA |  |  |  | 1000 |  | 0.77785 | 49350.3697
PACR 4 | Northern Hub and Roxby Downs | SA |  |  |  | 1000 |  | 0.56342 | 35745.6732
PACR 5 | Northern Hub and Yorke Peninsula | SA |  |  |  | 1000 |  | 0.38893 | 24675.1849
PACR 6 | Northern Hub and Eyre Peninsula | SA |  |  |  | 1000 |  | 0.64821 | 41125.3081
PACR 7 | Northern Hub, Leigh Creek and Roxby Downs | SA |  |  |  | 1000 |  | 1.082 | 68645.9197
PACR 8 | Northern Hub, Leigh Creek and Yorke Peninsula | SA |  |  |  | 1000 |  | 0.9075 | 57575.4313
PACR 9 | Northern Hub, Roxby Downs and Yorke Peninsula | SA |  |  |  | 1000 |  | 0.69306 | 43970.7348
PACR 10 | Northern Hub, Eyre Peninsula and Leigh Creek | SA |  |  |  | 1000 |  | 1.1668 | 74025.5546
PACR 11 | Northern Hub, Eyre Peninsula and Roxby Downs | SA |  |  |  | 1000 |  | 0.95235 | 60420.8581
PACR 12 | Northern Hub, Eyre Peninsula and Yorke Peninsula | SA |  |  |  | 1000 |  | 0.77785 | 49350.3697
PACR 13 | All North SA except Eyre Peninsula | SA |  |  |  | 1000 |  | 1.2116 | 76870.9813
PACR 14 | All North SA except Leigh Creek | SA |  |  |  | 1000 |  | 1.082 | 68645.9197
PACR 15 | All North SA except Roxby Downs | SA |  |  |  | 1000 |  | 1.2964 | 82250.6162
PACR 16 | All North SA except Yorke Peninsula | SA |  |  |  | 1000 |  | 1.4709 | 93321.1046
PACR 17 | All North SA | SA |  |  |  | 1000 |  | 1.6006 | 101546.1662 | [6 empty] | Cost to expand to Mid-North and Northern SA, and all branches leading from Northern SA
PACR 18 | SA Solar must be coupled with storage 1 for 1. (Column I for details) | [5 empty] | 0 |  |  | +450 [Note 1] | [5 empty] | Note 1: Option A storage allows for solar in South Australia without being stapled with additional stroage.

## Cycling of thermal plant
Cycling of thermal plant
Minimum operating and down times for thermal generators, used in time sequential modelling.
Generator | Minimum up time | Minimum down time
| Hours | Hours
CALL_B_1 | 120 | 12
CALL_B_2 | 120 | 12
CPP_3 | 120 | 12
CPP_4 | 120 | 12
GSTONE1 | 120 | 12
GSTONE2 | 120 | 12
GSTONE3 | 120 | 12
GSTONE4 | 120 | 12
GSTONE5 | 120 | 12
GSTONE6 | 120 | 12
KPP_1 |  | 12
MPP_1 | 120 | 12
MPP_2 | 120 | 12
STAN-1 | 120 | 12
STAN-2 | 120 | 12
STAN-3 | 120 | 12
STAN-4 | 120 | 12
TARONG1 | 120 | 12
TARONG2 | 120 | 12
TARONG3 | 120 | 12
TARONG4 | 120 | 12
TNPS1 | 120 | 12
BW01 |  | 12
BW02 |  | 12
BW03 |  | 12
BW04 |  | 12
ER01 | 120 | 12
ER02 | 120 | 12
ER03 | 120 | 12
ER04 | 120 | 12
LD01 |  | 12
LD02 |  | 12
LD03 |  | 12
LD04 |  | 12
MP1 | 120 | 12
MP2 | 120 | 12
VP5 | 120 | 12
VP6 | 120 | 12
WW7 | 120 | 12
WW8 | 120 | 12
LOYYB1 |  | 12
LOYYB2 |  | 12
LYA1 |  | 12
LYA2 |  | 12
LYA3 |  | 12
LYA4 |  | 12
YWPS1 | 120 | 12
YWPS2 |  | 12
YWPS3 |  | 12
YWPS4 |  | 12
OSB-AG | 24 | 12
PPCCGT | 24 | 12
TORRA1 | 24 | 12
TORRA2 | 24 | 12
TORRA3 | 24 | 12
TORRA4 | 24 | 12
TORRB1 | 24 | 12
TORRB2 | 24 | 12
TORRB3 | 24 | 12
TORRB4 | 24 | 12

## Inertia
Inertia
Inertia Source | Inertia (MW.s)
Torrens Island B1-B4 | 900
Torrens Island A1-A2 | 795
Pelican Point (all units) | 4769
Osborne (all units) | 1512
Quarantine 1-4 | 89
Quarantine 5 | 1030
Dry Creek 1-3 | 526
Hallett (all units) | 598
Base case (2*synchronous condenser ) | 1300
Pumped Hydro | ~ 1000
Solar thermal | ~ 500
Each additional synchronous condenser | 650
100 MW Battery (assumed response time 250 ms) | 380

## DSP
Demand-side Participation (MW)
Electricity demand that will be removed from the market when modelled prices reach specified limits
Price band | NSW | QLD | SA | TAS | VIC Summer | VIC Winter
Prices > $300/MWh | 38.3 | 27.3 | 15.4 | 4.9 | 76.7 | 76.7
Prices > $500/MWh | 50.2 | 27.9 | 16.6 | 4.9 | 79 | 79
Prices > $1000/MWh | 53.2 | 28.6 | 17.2 | 4.9 | 81.5 | 81.5
Prices > $7500/MWh | 61 | 82.6 | 88.1 | 15.2 | 141.8 | 85
Prices = MPC | 248.5 | 147.5 | 120.2 | 43 | 141.8 | 85
Estimated DSP for Queensland LNG
QLD addition
Prices > $300/MWh | 0
Prices > $500/MWh | 0
Prices > $1000/MWh | 0
Prices > $7500/MWh | 0
Prices = MPC | 300

## Battery aggregation
Battery aggregation
Aggregation of household battery installations by NEM participants for arbitrage and emergency response
Neutral capacity growth (all small-scale batteries, MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | 51.2 | 132.4 | 251.1 | 408.3 | 565 | 720.3 | 876.4 | 1030.7 | 1179.3 | 1324.4 | 1465.4 | 1602.2 | 1736.7 | 1851.5 | 1943.8 | 2031.8 | 2121 | 2209.4 | 2299.2 | 2387.5 | 2474.5 | 2518.3 | 2606.6
QLD | 27.5 | 71.2 | 136.7 | 225.3 | 305.5 | 380 | 448.3 | 512.4 | 572.4 | 630.8 | 688.7 | 745.9 | 802.8 | 859.3 | 915.6 | 970.5 | 1025.3 | 1080 | 1132 | 1181.5 | 1228.6 | 1272.5 | 1314.5
SA | 9.3 | 24.2 | 46.9 | 77.3 | 107.7 | 138 | 168.3 | 199.7 | 231 | 262.3 | 293.6 | 324.9 | 356.3 | 386.6 | 414.8 | 440.8 | 461.5 | 480.1 | 498.8 | 516 | 533.3 | 550.5 | 567.7
TAS | 2.3 | 5.8 | 11.1 | 17.5 | 23.4 | 29.7 | 33.2 | 35.4 | 36.4 | 37.4 | 38.1 | 38.7 | 39.3 | 39.9 | 40.6 | 41.2 | 41.9 | 42.6 | 43.2 | 43.9 | 44.6 | 45.3 | 46
VIC | 29.1 | 78.6 | 155.4 | 249 | 322.1 | 388.2 | 449.2 | 510.1 | 568.8 | 626.2 | 680.9 | 734.5 | 788.4 | 842.8 | 897.6 | 951.5 | 1001.7 | 1048.5 | 1092.4 | 1133 | 1171 | 1206.2 | 1239.4
Aggregation trajectories
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
45% | 0% | 6% | 10% | 14% | 17% | 20% | 22% | 25% | 27% | 29% | 30% | 32% | 33% | 34% | 35% | 36% | 37% | 38% | 39% | 40% | 40% | 41% | 41%
90% | 0% | 11% | 20% | 27% | 34% | 40% | 45% | 49% | 53% | 57% | 60% | 63% | 66% | 68% | 71% | 73% | 75% | 76% | 78% | 79% | 80% | 82% | 83%
10% | 0% | 1% | 2% | 3% | 4% | 4% | 5% | 5% | 6% | 6% | 7% | 7% | 7% | 8% | 8% | 8% | 8% | 8% | 9% | 9% | 9% | 9% | 9%
Neutral capacity growth, 45% aggregation by 2050 (MW)
| 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40
NSW | - | 7.5 | 25.2 | 56.1 | 95.9 | 142.8 | 196.1 | 254 | 314.6 | 377.6 | 442.1 | 507.3 | 573.4 | 634 | 687.3 | 739.1 | 791.1 | 842.7 | 894.6 | 945.7 | 996 | 1028.4 | 1078.4
QLD | - | 4 | 13.7 | 30.9 | 51.8 | 75.4 | 100.3 | 126.3 | 152.7 | 179.9 | 207.7 | 236.2 | 265 | 294.3 | 323.8 | 353 | 382.4 | 411.9 | 440.4 | 468 | 494.5 | 519.6 | 543.8
SA | - | 1.4 | 4.7 | 10.6 | 18.3 | 27.4 | 37.6 | 49.2 | 61.6 | 74.8 | 88.6 | 102.9 | 117.6 | 132.4 | 146.7 | 160.4 | 172.1 | 183.1 | 194.1 | 204.4 | 214.6 | 224.8 | 234.9
TAS | - | 0.3 | 1.1 | 2.4 | 4 | 5.9 | 7.4 | 8.7 | 9.7 | 10.7 | 11.5 | 12.2 | 13 | 13.7 | 14.3 | 15 | 15.6 | 16.2 | 16.8 | 17.4 | 17.9 | 18.5 | 19
VIC | - | 4.5 | 15.6 | 34.2 | 54.7 | 77 | 100.5 | 125.7 | 151.8 | 178.5 | 205.4 | 232.5 | 260.3 | 288.6 | 317.4 | 346.1 | 373.6 | 399.9 | 425 | 448.8 | 471.3 | 492.5 | 512.7

## Build cost
Build cost ($/kW) real 2019 dollars
Cost to construct new generation, not including connection costs. Battery installations assume energy storage of 2kWh/kW. Pumped hydro installations assume energy storage of 6kWh/kW
Slow and rapid scenarios use the Neutral cost trajectories, except for technologies specified
Central | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45 | 2045-46 | 2046-47 | 2047-48 | 2048-49 | 2049-50
Biomass | 3919.4994 | 3910.8659 | 3897.2012 | 3895.411 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3892.1516 | 3891.9158 | 3891.5057 | 3891.4954 | 3891.4842 | 3891.4557 | 3891.4436 | 3891.4311 | 3891.4181 | 3891.4181 | 3891.3844 | 3891.3844 | 3891.3844 | 3891.3844 | 3891.321 | 3891.3034 | 3891.2853 | 3891.2853 | 3891.2853 | 3891.2289
CCGT | 1556.4173 | 1556.3943 | 1556.3943 | 1556.1372 | 1556.0225 | 1555.6964 | 1555.3822 | 1555.0794 | 1554.7878 | 1554.106 | 1553.0649 | 1552.0626 | 1551.0976 | 1550.1689 | 1549.2751 | 1548.4152 | 1547.5881 | 1546.7926 | 1546.0277 | 1545.6631 | 1544.0865 | 1542.5743 | 1541.1242 | 1539.7338 | 1538.4009 | 1537.1232 | 1535.8987 | 1534.7253 | 1533.6012 | 1532.1082 | 1530.3849 | 1530.3849 | 1530.3849
OCGT | 1057.4734 | 1052.186 | 1046.9251 | 1041.6905 | 1036.482 | 1031.2996 | 1026.1431 | 1021.0124 | 1015.9073 | 1010.8278 | 1005.7737 | 1000.7448 | 995.7411 | 990.7624 | 985.8085 | 980.8795 | 975.9751 | 971.0952 | 966.2398 | 961.4086 | 956.6015 | 951.8185 | 947.0594 | 942.3241 | 937.6125 | 932.9244 | 928.2598 | 923.6185 | 919.0004 | 914.4054 | 909.8334 | 905.2842 | 900.7578
Single-axis Tracking Solar PV | 2024.5446 | 1797.6165 | 1695.375 | 1547.9282 | 1474.1794 | 1413.6327 | 1365.5202 | 1317.2309 | 1274.2176 | 1227.719 | 1190.9089 | 1121.7136 | 1072.0832 | 1026.4014 | 989.0923 | 947.3329 | 902.7103 | 882.1368 | 846.7533 | 827.9743 | 810.6386 | 794.5794 | 779.5854 | 765.1173 | 752.2946 | 741.4188 | 729.4081 | 718.0415 | 706.9398 | 699.1775 | 691.1749 | 682.7929 | 676.6523
Solar Thermal Central Receiver (6 hrs storage) | 4599.0937 | 3814.1992 | 3421.7225 | 3421.7225 | 3421.7225 | 3421.7225 | 3421.7225 | 3421.7225 | 3418.7223 | 3254.0016 | 3144.3682 | 3013.2164 | 2941.3146 | 2898.0427 | 2893.3846 | 2792.7944 | 2720.1409 | 2665.2512 | 2622.3574 | 2587.9448 | 2559.7499 | 2536.2488 | 2516.3781 | 2499.3731 | 2484.6698 | 2471.8431 | 2460.5664 | 2420.8025 | 2384.2911 | 2351.6044 | 2322.2021 | 2295.6407 | 2271.553
Wind | 2017.2926 | 2012.4786 | 2005.7532 | 1996.2643 | 1992.4464 | 1979.4589 | 1971.8824 | 1970.2209 | 1969.6247 | 1969.5361 | 1969.4397 | 1969.2856 | 1945.6262 | 1921.3726 | 1905.3825 | 1892.405 | 1882.274 | 1863.1453 | 1831.5703 | 1820.1217 | 1809.8133 | 1800.8348 | 1792.4321 | 1774.3039 | 1770.5803 | 1767.4904 | 1764.9295 | 1762.7462 | 1759.3642 | 1754.1655 | 1747.3647 | 1741.5622 | 1736.7712
Pumped Hydro (6hrs storage) | 1437.5897 | 1430.4018 | 1423.2497 | 1416.1335 | 1409.0528 | 1402.0076 | 1394.9975 | 1388.0225 | 1381.0824 | 1374.177 | 1367.3061 | 1360.4696 | 1353.6673 | 1346.8989 | 1340.1644 | 1333.4636 | 1326.7963 | 1320.1623 | 1313.5615 | 1306.9937 | 1300.4587 | 1293.9564 | 1287.4866 | 1281.0492 | 1274.644 | 1268.2707 | 1261.9294 | 1255.6197 | 1249.3416 | 1243.0949 | 1236.8795 | 1230.6951 | 1224.5416
Large Scale Battery Storage (2hrs storage) | 1535.1486 | 1361.9028 | 1253.2682 | 1210.0971 | 1185.8896 | 1162.3429 | 1140.1889 | 1118.258 | 1096.5641 | 1075.2871 | 1045.5423 | 1023.639 | 1002.9247 | 983.526 | 963.5079 | 943.9754 | 924.6217 | 905.5726 | 888.1561 | 871.5632 | 855.6057 | 840.347 | 825.4351 | 810.9446 | 796.6779 | 782.3124 | 768.6474 | 755.3468 | 742.4277 | 729.7132 | 717.2915 | 705.132 | 693.222
Black Coal (HELE) | 3389.8028 | 3385.1008 | 3370.103 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5915 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873 | 3353.5873
Economic Life | Years
Biomass | 30
CCGT | 30
OCGT | 30
Single-axis Tracking Solar PV | 30
Wind | 20

## Connection cost
Initial connection costs ($/kW) real 2019 dollars
Build costs are adjusted according to NEM planning zone to account for proximity to transmission assets
Final connection costs will be subject to modelling outcomes
Renewable Energy Zone | Wind | Solar | Biomass | Batteries | Pumped hydro | NEM Zone | Gas
Broken Hill | 105.25 | 105.25 | 0 | 105.25 | 105.25 | NQ | 86.4021
Central NSW Tablelands | 94.725 | 105.25 | 84.2 | 105.25 | 105.25 | CQ | 86.4021
Central West NSW | 94.725 | 105.25 | 84.2 | 105.25 | 105.25 | SWQ | 84.9891
Murray River | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | SEQ | 86.4021
North West NSW | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | NNS | 80.766
Northern NSW Tablelands | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | NCEN | 78.3547
Riverland | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | CAN | 76.9125
Southern NSW Tablelands | 105.25 | 84.2 | 84.2 | 105.25 | 105.25 | SWNSW | 80.766
Barcaldine | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | NVIC | 69.5268
Darling Downs | 100.2957 | 74.3655 | 84.2 | 105.25 | 105.25 | LV | 68.0769
Fitzroy | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | MEL | 84.9891
Isaac | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | CVIC | 84.9891
North Qld Clean Energy Hub | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | NSA | 73.675
Northern Qld | 105.25 | 105.25 | 84.2 | 105.25 | 105.25 | ADE | 73.675
Eastern Eyre Peninsula | 136.825 | 84.2 | 84.2 | 105.25 | 105.25 | SESA | 199.9749
Leigh Creek | 136.825 | 84.2 | 0 | 105.25 | 0 | TAS | 94.725
Mid-North SA | 136.825 | 84.2 | 84.2 | 105.25 | 105.25
Northern SA | 136.825 | 84.2 | 84.2 | 105.25 | 105.25
Roxby Downs | 136.825 | 84.2 | 0 | 105.25 | 105.25
South East SA | 178.9249 | 178.9249 | 84.2 | 105.25 | 0 | NEM Region | Gas | Shadow NEM zone for Gas | Black Coal (HELE)
Western Eyre Peninsula | 136.825 | 84.2 | 84.2 | 105.25 | 105.25
Yorke Peninsula | 136.825 | 84.2 | 84.2 | 105.25 | 105.25 | TAS | 94.725 | TAS
King island | 126.3 | 126.3 | 0 | 105.25 | 105.25 | QLD | 86.4021 | NQ/CQ/SEQ | 141.4034
North East Tasmania | 126.3 | 126.3 | 84.2 | 105.25 | 105.25 | SA | 73.675 | NSA/ADE
North West Tasmania | 126.3 | 126.3 | 84.2 | 105.25 | 105.25 | NSW | 80.766 | NNS/SWNSW | 141.4034
Tasmania Midlands | 126.3 | 126.3 | 84.2 | 105.25 | 105.25 | VIC | 68.0769 | LV
Gippsland | 126.3 | 126.3 | 84.2 | 105.25 | 105.25
Moyne | 115.775 | 94.725 | 84.2 | 105.25 | 105.25 | 1. Regional connection costs for gas are derived from shadow NEM zone connection cost.
Western Victoria | 115.775 | 94.725 | 84.2 | 105.25 | 105.25
ElectraNet has not added new entrant Gas generators by NEM zone, only per Region
Missing values denote generators not added

## Maximum capacity
Maximum capacity
Maximum capacity is used to report capacity factors and calculate fixed operating costs. It may not correspond to "installed capacity" listed in Generation Information workbooks, when maximum seasonal ratings differ.
Existing Generators |  | Committed Projects
Generator | Installed capacity (MW) | Generator | Installed capacity (MW) | Indicative commissioning date
Bayswater | 2640 | Barker Inlet | 216 | 2019-03-01
Eraring | 2880 | Bodangora WF | 113 | 2018-08-01
Liddell | 1800 | Crookwell 2 WF | 91 | 2018-09-01
Mount Piper | 1400 | Sapphire WF | 270 | 2018-07-01
Vales Point | 1320 | Silverton WF | 199 | 2018-07-01
Callide B | 700 | Mt Emerald | 180 | 2018-09-01
Callide Power Plant | 900 | BULGANAWF | 196 | 2019-07-01
Gladstone | 1680 | CROWLANDSWF | 80 | 2019-07-01
Kogan Creek | 744 | Mt Gellibrand WF | 132 | 2018-06-01
Millmerran | 852 | Salt Creek WF | 54 | 2018-07-01
Stanwell | 1460 | Stockyard Hill WF | 530 | 2019-12-01
Tarong | 1400 | Griffith Solar | 30 | 2019-01-01
Tarong North | 443 | Manildra Solar | 50 | 2018-07-01
Loy Yang A | 2210 | Clare Solar | 150 | 2018-05-01
Loy Yang B | 1070 | Hamilton Solar | 58 | 2018-03-01
Yallourn | 1528 | Oakey Solar | 25 | 2018-08-01
Colongra | 724 | Ross River Solar | 116 | 2018-05-01
Smithfield1 | 109 | Rugby Run Solar | 65 | 2019-01-01
Tallawarra | 440 | Sun Metals Solar | 125 | 2018-04-01
Uranquinty | 688 | Teebar Solar | 53 | 2018-03-01
Barcaldine | 37 | Whitsunday Solar | 58 | 2018-03-01
Braemar | 1023 | Bannerton Solar | 88 | 2018-06-01
Condamine | 100 | Gannawarra Solar | 55 | 2018-04-01
Darling Downs | 633 | Karadoc Solar | 90 | 2018-04-01
Oakey | 346 | Wemen Solar | 88 | 2018-02-01
Roma | 68 | Yatpool Solar | 81 | 2018-04-01
Swanbank E2 | 365 | Bungala Solar | 110 | 2018-08-01
Yabulu | 243 | Bungala Solar Stage 2 | 110 | 2019-01-01
Yarwun | 180 | Tailem Bend Solar | 100 | 2019-07-01
Somerton | 162 | Collinsville Solar Power Station | 43 | 2019-01-01
Bairnsdale | 84 | Darling Downs Solar | 110 | 2018-09-01
Jeeralang A | 224 | Kennedy Energy Park Solar | 15 | 2018-12-01
Jeeralang B | 255 | Kennedy Energy Park Wind | 43 | 2018-12-01
Laverton North | 340 | Lilyvale Solar | 100 | 2019-01-01
Mortlake | 584 | Coopers Gap WF | 453 | 2019-06-01
Newport | 510 | Lincoln Gap Wind Farm | 126 | 2018-10-01
Valley Power | 336 | Willogoleche WF | 119 | 2018-08-01
Hallett GT | 216 | Beryl Solar | 100 | 2019-07-01
Dry Creek | 143 | Daydream Solar | 167 | 2018-08-01
Ladbroke Grove | 84 | Hayman Solar | 58 | 2018-05-01
Mintaro | 90
Osborne | 188
Pelican Point | 474
Quarantine | 220
Torrens Island A | 480
Torrens Island B | 800
Bell Bay Three | 105
Tamar Valley CCGT | 208
Tamar Valley OCGT | 58
Hunter Valley GT | 50
Mackay GT | 34
Mount Stuart | 423
Angaston | 50
Lonsdale | 21
Port Lincoln | 50
Port Lincoln 3 | 24
Port Stanvac | 58
Snuggery | 63
Blowering | 80
Guthega | 68
Hume | 58
Shoalhaven | 240
Tumut 1 | 328
Tumut 2 | 288
Tumut 3 | 1800
Barron Gorge | 66
Kareeya | 86
Wivenhoe | 500
Bogong | 150
Dartmouth | 170
Eildon | 113
McKay Creek | 150
Murray 1 | 950
Murray 2 | 560
West Kiewa | 68
Bastyan | 81
Catagunya | 50
Cethana | 95
Devils Gate | 63
Fisher | 46
Gordon | 371
John Butters | 140
Liapootah | 84
Lake Echo | 30
Lemonthyme | 54
Mackintosh | 81
Meadowbank | 44
Poatina | 342
Reece | 232
Tarraleah | 90
Trevallyn | 103
Tribute | 88
Tungatinah | 131
Wilmot | 31
Wayatinah | 38
Boco Rock WF | 113
Capital WF | 141
Cullerin Range WF | 30
Gullen Range WF | 166
Gunning WF | 47
Taralga WF | 107
Woodlawn WF | 48
Ararat WF | 240
Bald Hills WF | 107
Challicum Hills WF | 53
Macarthur WF | 420
Mortons Lane | 20
Mount Mercer WF | 131
Oaklands Hill WF | 63
PWEP 1 Yambuk WF | 30
PWEP 2 Cape Bridgewater WF | 58
PWEP 3 Cape Nelson South WF | 44
PWEP 4 Cape Nelson North WF | 47
Waubra WF | 192
Canunda WF | 46
Cathedral Rocks WF | 66
Clements Gap WF | 57
Hallett 1 Brown Hill WF | 95
Hallett 2 Hallett Hill WF | 74
Hallett 4 North Brown Hill WF | 132
Hallett 5 The Bluff WF | 53
Hornsdale S1 WF | 100
Hornsdale S2 WF | 100
Hornsdale S3 WF | 109
Lake Bonney 1 WF | 81
Lake Bonney 2 WF | 159
Lake Bonney 3 WF | 39
Mount Millar WF | 70
Snowtown 1 WF | 99
Snowtown 2 North WF | 144
Snowtown 2 South WF | 126
Starfish Hill WF | 35
Waterloo WF | 131
Wattle Point WF | 91
Musselroe WF | 168
Woolnorth WF | 140
Broken Hill Solar Plant | 53
Moree Solar | 56
Nyngan Solar | 102
Parkes Solar | 91
Kidston Solar | 50
White Rock WF | 175
Kiata WF | 31
1. Smithfield operating as a fast start OCGT from late 2017
2. Swanbank E return to service in 2018

## Generation limits
Generation limits
The following modelling assumptions are based on AEMO analysis of historical generator performance.
Generator | Minimum Load (MW) | Generator | Minimum Capacity Factor | End time | Generator | Max Capacity Factor
BW01 | 310.5 | Osborne* | 60% | Depending on timing of SA interconnector expansion | Liddell | 50%
BW02 | 310.5 | Pelican Point* | 50% | Depending on timing of SA interconnector expansion
BW03 | 310.5 | Torrens Island B* | 25% | Until retirement
BW04 | 310.5
ER01 | 230
ER02 | 230
ER03 | 230
ER04 | 230
LD01 | 260
LD02 | 260
LD03 | 260
LD04 | 260
MP1 | 280
MP2 | 280
VP5 | 250
VP6 | 250
CALL_B_1 | 175
CALL_B_2 | 175
CPP_3 | 225
CPP_4 | 225
GSTONE1 | 120
GSTONE2 | 120
GSTONE3 | 120
GSTONE4 | 120
GSTONE5 | 120
GSTONE6 | 120
KPP_1 | 362
MPP_1 | 170
MPP_2 | 170
STAN-1 | 180
STAN-2 | 180
STAN-3 | 180
STAN-4 | 180
TARONG#1 | 175
TARONG#2 | 175
TARONG#3 | 175
TARONG#4 | 175
TNPS1 | 220
LOYYB1 | 240
LOYYB2 | 240
LYA1 | 410
LYA2 | 300
LYA3 | 410
LYA4 | 410
YWPS1 | 216
YWPS2 | 216
YWPS3 | 228
YWPS4 | 228
CPSA | 60
YARWUN_1 | 118
Torrens Island A | 30
Torrens Island B | 40
Dry Creek | 10
Hallett GT | 16
Ladbroke Grove | 30
Mintaro | 30
Osborne | 128
Pelican Point | 240
Quarantine | 10

## Minimum Reserve Levels
Minimum Reserve Levels
Region | Minimum Reserve Level (MW)
NSW | 1173.2
QLD | 666.08
SA | 273
TAS | 194
VIC | 498

## Interconnector Firm Capacity
Interconnector Firm Capacity
Option | Interconnector | Notional capacity | Combined limit Note 2 | Capability during a prior outage Note 1 | Firm capacity (combined limit during a prior outage) | Net increase in firm capacity improvement
Base | Heywood | 650 | - | 50 |  | -
Option B1 | Heywood | 750 | 1300 | 300 | 850 | 800
| SA - Queensland | 700 | 1300 | 300
Option C3 | Heywood | 750 | 1300 | 300 | 850 | 800
| SA - NSW | 800 |  | 300
Option D1 | Heywood | 750 | 1150 | 300 | 850 | 650
| SA - Vic (via Horsham) | 650 |  | 300
Note 1 - Capability after a credible contingency event or during a prior outage along that corridor.
Note 2 - Combined limits assume 400 MW of load shedding for a non-credible event on either interconnector. Further details can be found in the technical assumptions report.

## QRET
Queensland Renewable Energy Target
50% of Queensland consumption to be provided by large-scale renewable generation by 2030 target
Financial year | Energy (GWh)
2020-21 | -
2021-22 | -
2022-23 | 2400
2023-24 | 4700
2024-25 | 7200
2025-26 | 10100
2026-27 | 12600
2027-28 | 15200
2028-29 | 17800
2029-30 | 20500
Trajectory of total large scale generation of renewable energy required, including Q400 auction eligible, as calculated by the QLD Government Expert Panel report: https://www.dnrm.qld.gov.au/__data/assets/pdf_file/0018/1259010/qreep-renewable-energy-target-report.pdf
To deliver reasonable technological diversity, wind generation is assumed to provide at least 25% of the annual targets

## VRET
Victorian Renewable Energy Target
25% renewable energy generation by 2020, 40% renewable energy generation by 2025
New entry renewable capacity (MW)
| Solar | Wind | Total
2019-20 | 200 | 500 | 700
2020-21 | 360 | 900 | 1260
2021-22 | 520 | 1300 | 1820
2022-23 | 680 | 1700 | 2380
2023-24 | 840 | 2100 | 2940
2024-25 | 1000 | 2500 | 3500

## Emission Trajectory
Emissions Target Trajectories
Emissions reduction targets are expressed as a percentage of total emissions across all sectors. This table includes electricity NEM generation emissions only.
Financial Year | 28% to 70% Emissions Reduction Target | 52% to 90% Emissions Reduction Target
(Mt CO2-e)
2020-21 | 142 | 142
2021-22 | 140.5296 | 136.2446
2022-23 | 139.0592 | 130.4891
2023-24 | 137.5887 | 124.7337
2024-25 | 136.1183 | 118.9783
2025-26 | 134.6479 | 113.2228
2026-27 | 133.1775 | 107.4674
2027-28 | 131.7071 | 101.712
2028-29 | 130.2366 | 95.9566
2029-30 | 128.7662 | 90.2011
2030-31 | 127.2958 | 84.4764
2031-32 | 123.3412 | 81.065
2032-33 | 119.3866 | 77.6536
2033-34 | 115.4319 | 74.2423
2034-35 | 111.4773 | 70.8309
2035-36 | 107.5227 | 67.4195
2036-37 | 103.5681 | 64.0081
2037-38 | 99.6134 | 60.5968
2038-39 | 95.6588 | 57.1854
2039-40 | 91.7042 | 53.774
2040-41 | 87.7496 | 50.3627
2041-42 | 83.7949 | 46.9513
2042-43 | 79.8403 | 43.5399
2043-44 | 75.8857 | 40.1285
2044-45 | 71.9311 | 36.7172
2045-46 | 67.9764 | 33.3058
2046-47 | 64.0218 | 29.8944
2047-48 | 60.0672 | 26.483
2048-49 | 56.1125 | 23.0717
2049-50 | 52.1579 | 19.6603
2030 emissions reduction targets are calculated from 2005 levels.
2050 emissions reduction targets are calculated from 2005 levels for the 90% trajectory, and 2016 levels for the 70% trajectory.
The emissions trajectory starts at estimated emissions for 2020-21.

## Interconnector Capability
Interconnector Transfer Capability (MW)
Interconnector transfer limits used in capacity expansion modelling.
Interconnector | Forward Direction | Forward capability | Reverse Capability | Effective from
QNI [Note 1] | NSW to QLD | 310 | 1025
QNI - ISP Option 3 | NSW to QLD | 770 | 1215 | 2020
QNI - ISP Option 5 | NSW to QLD | 770 | 1593 | 2023
Terranora | NSW to QLD | 50 | 150
VIC-NSW | VIC to NSW | 700 | 400
Heywood | VIC to SA | 650 | 650
Murraylink [Note 2] | VIC to SA | 220 | 200
Basslink | TAS to VIC | 478 | 478
Note 1: See QNI Augmentations for details on changes to QNI for Option B.
Note 2. Forward capability is limited by thermal limitations in the Victorian 220 kV transmission network which are removed with the preferred option. Reverse capability is limited by thermal limitations in the South Australian 132 kV transmission network.

## QNI Augmentations
QNI Augmentations
Option B
Option label | Project description | Forward Direction | Notional Limit |  | Cost Estimate ($ millions) | Earliest commissioning year
|  |  | Forward direction | Reverse direction
Current | Initial capability | NSW to QLD | 310 | 1025
QNI-Option 3 | Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Install SVCs at Dumaresq and Tamworth substations. Install shunt capacitor banks at Tamworth, Armidale and Dumaresq substations. | NSW to QLD | 770 [+460] | 1,215 [+190] | 142 | 2020-07-01
QNI-Option 5 | New Armidale-Bulli Creek HVAC at 330 kV Install Armidale-Dumaresq and Dumaresq-Bulli Creek additional new 330 kV double circuit line. Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Augment existing substations/switching stations at Armidale, Dumaresq and Bulli Creek. | NSW to QLD | 770 | 1,593 [+368] | 560 | 2023-07-01
Option B | HVDC South Australia to Queensland | NSW to QLD | 1,020 [+250] | 1,843 [+250] |  | 2024-07-01
ISP QNI 5 Deferral
Option label | Project description | Forward Direction | Notional Limit |  | Cost Estimate ($ millions) | Earliest commissioning year
|  |  | Forward direction | Reverse direction
Current | Initial capability | NSW to QLD | 310 | 1025
QNI-Option 3 | Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Install SVCs at Dumaresq and Tamworth substations. Install shunt capacitor banks at Tamworth, Armidale and Dumaresq substations. | NSW to QLD | 770 [+460] | 1,215 [+190] | 142 | 2020-07-01
Option B | HVDC South Australia to Queensland | NSW to QLD | 1,020 [+250] | 1,465 [+250] |  | 2024-07-01
QNI-Option 5 | New Armidale-Bulli Creek HVAC at 330 kV Install Armidale-Dumaresq and Dumaresq-Bulli Creek additional new 330 kV double circuit line. Uprating of Liddell-Muswellbrook (#83), Muswellbrook-Tamworth (#88) and Liddell-Tamworth (#84) 330 kV lines. Augment existing substations/switching stations at Armidale, Dumaresq and Bulli Creek. | NSW to QLD | 1020 | 1,843 [+368] | 560 | 2033-07-01

## Storage properties
Storage properties
Battery properties
Property | Value
Maximum power1 | 1 | MW
Energy capacity | 2 | MWh
Charge efficiency (household) | 90%
Charge efficiency (utility) | 80%
Technical life | 15 | years
Initial SOC | 20%
1. Power and capacity are defined as a 1:2 ratio. The model is free to build utility-scale batteries up to defined build limits
Pumped hydro properties
Property | Value
Maximum power | 100 | MW
Energy capacity | 6 | hours
Pump efficiency | 80%
Economic life | 50 | years
Initial SOC | 20%

## Coal and Biomass price
Coal and Biomass price ($/GJ, real 2019 dollars)
Generator | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bayswater | 1.5267 | 1.5674 | 1.659 | 1.659 | 1.6794 | 1.7303 | 1.7812 | 1.8524 | 1.8524 | 2.0356 | 2.4427 | 2.7073 | 2.8397 | 2.9414 | 2.9822 | 3.033 | 3.0839 | 3.1552 | 3.1959 | 3.1959 | 3.1959 | 3.1959 | 3.1959 | 3.1959
Eraring | 2.3817 | 2.5343 | 2.7175 | 2.8906 | 2.9516 | 3.0025 | 3.0839 | 3.2366 | 3.3689 | 3.3995 | 3.5012 | 3.6234 | 3.7557 | 3.8473 | 3.9084 | 3.9694 | 4.0407 | 4.1323 | 4.1832 | 4.1832 | 4.1832 | 4.1832 | 4.1832 | 4.1832
Liddell | 1.5267 | 1.5674 | 1.659 | 1.659 | 1.6794 | 1.7303 | 1.7812 | 1.8524 | 1.8524 | 2.0356 | 2.4427 | 2.7073 | 2.8397 | 2.9414 | 2.9822 | 3.033 | 3.0839 | 3.1552 | 3.1959 | 3.1959 | 3.1959 | 3.1959 | 3.1959 | 3.1959
Mount Piper | 2.0661 | 2.1577 | 2.3206 | 2.4427 | 2.4936 | 2.5547 | 2.6157 | 2.7582 | 2.8702 | 2.9516 | 3.1043 | 3.2264 | 3.3689 | 3.4911 | 3.5419 | 3.5827 | 3.6335 | 3.715 | 3.7659 | 3.7659 | 3.7659 | 3.7659 | 3.7659 | 3.7659
Vales Point | 2.29 | 2.4325 | 2.6157 | 2.7888 | 2.8498 | 3.0025 | 3.0839 | 3.2366 | 3.3689 | 3.3995 | 3.5012 | 3.6234 | 3.7557 | 3.8473 | 3.9084 | 3.9694 | 4.0407 | 4.1323 | 4.1832 | 4.1832 | 4.1832 | 4.1832 | 4.1832 | 4.1832
Callide B | 2.0763 | 2.0763 | 2.117 | 2.1577 | 2.1984 | 2.2188 | 2.2392 | 2.2595 | 2.3104 | 2.3409 | 2.3511 | 2.3817 | 2.4122 | 2.4631 | 2.7175 | 2.9516 | 3.0127 | 3.0941 | 3.1246 | 3.1246 | 3.1246 | 3.1246 | 3.1246 | 3.1246
Callide Power Plant | 2.0763 | 2.0763 | 2.117 | 2.1577 | 2.1984 | 2.2188 | 2.2392 | 2.2595 | 2.3104 | 2.3409 | 2.3511 | 2.3817 | 2.4122 | 2.4631 | 2.7175 | 2.9516 | 3.0127 | 3.0941 | 3.1246 | 3.1246 | 3.1246 | 3.1246 | 3.1246 | 3.1246
Gladstone | 2.3002 | 2.4834 | 2.7175 | 2.86 | 2.9109 | 2.9822 | 3.0534 | 3.2061 | 3.3282 | 3.3587 | 3.4198 | 3.5216 | 3.6743 | 3.7659 | 3.8168 | 3.8778 | 3.9491 | 4.0407 | 4.0916 | 4.0916 | 4.0916 | 4.0916 | 4.0916 | 4.0916
Kogan Creek | 1.5674 | 1.5776 | 1.5878 | 1.5878 | 1.5878 | 1.6081 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285 | 1.6285
Millmerran | 1.3028 | 1.3028 | 1.3028 | 1.313 | 1.313 | 1.3231 | 1.3435 | 1.3435 | 1.3435 | 1.3435 | 1.3435 | 1.3435 | 1.3435 | 1.3435 | 1.3435 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 1.3537 | 1.3639 | 1.3639 | 1.3639
Stanwell | 2.2188 | 2.3206 | 2.402 | 2.4631 | 2.4936 | 2.514 | 2.5343 | 2.5547 | 2.575 | 2.7277 | 3.1043 | 3.3893 | 3.5318 | 3.6641 | 3.715 | 3.7659 | 3.8269 | 3.9287 | 3.9694 | 3.9694 | 3.9694 | 3.9694 | 3.9694 | 3.9694
Tarong | 2.8397 | 2.8397 | 2.8498 | 2.86 | 2.86 | 2.8804 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007
Tarong North | 2.8397 | 2.8397 | 2.8498 | 2.86 | 2.86 | 2.8804 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007 | 2.9007
Loy Yang A | 0.63104 | 0.63104 | 0.66157 | 0.66157 | 0.66157 | 0.66157 | 0.67175 | 0.67175 | 0.67175 | 0.67175 | 0.68193 | 0.68193 | 0.68193 | 0.6921 | 0.6921 | 0.70228 | 0.70228 | 0.71246 | 0.71246 | 0.72264 | 0.72264 | 0.73282 | 0.74299 | 0.74299
Loy Yang B | 0.63104 | 0.63104 | 0.66157 | 0.66157 | 0.66157 | 0.66157 | 0.67175 | 0.67175 | 0.67175 | 0.67175 | 0.68193 | 0.68193 | 0.68193 | 0.6921 | 0.6921 | 0.70228 | 0.70228 | 0.71246 | 0.71246 | 0.72264 | 0.72264 | 0.73282 | 0.74299 | 0.74299
Yallourn | 0.63104 | 0.63104 | 0.64121 | 0.65139 | 0.65139 | 0.66157 | 0.66157 | 0.66157 | 0.66157 | 0.67175 | 0.67175 | 0.67175 | 0.68193 | 0.68193 | 0.68193 | 0.6921 | 0.6921 | 0.70228 | 0.70228 | 0.71246 | 0.71246 | 0.72264 | 0.73282 | 0.73282
Higher coal sensitivity | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bayswater | 1.5267 | 1.5674 | 1.659 | 1.659 | 1.6794 | 1.7303 | 1.7812 | 1.8524 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Eraring | 2.3817 | 2.5343 | 2.7175 | 2.8906 | 2.9516 | 3.0025 | 3.0839 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Mount Piper | 2.0661 | 2.1577 | 2.3206 | 2.4427 | 2.4936 | 2.5547 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Vales Point | 2.29 | 2.4325 | 2.6157 | 2.7888 | 2.8498 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
Biomass price | 2017-18 | 2018-19 | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Biomass | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089 | 0.5089

## Gas and liquid fuel price
Gas price ($/GJ, real 2019 dollars)
Prices are the sum of wholesale price and transportation cost.
Central
Generator | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bairnsdale | 10.8999 | 11.4185 | 10.8999 | 10.6632 | 10.4265 | 10.1897 | 9.953 | 9.953 | 9.953 | 9.953 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355
Barcaldine | 10.0516 | 10.0516 | 10.0516 | 9.7037 | 9.3558 | 9.008 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601 | 8.6601
Barker Inlet | 9.8528 | 9.8528 | 9.8528 | 9.5569 | 9.2609 | 8.9649 | 8.669 | 8.6934 | 9.5063 | 9.5062 | 9.5059 | 9.5062 | 9.5062 | 9.5061 | 9.5061 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506
Bell Bay Three | 10.3714 | 10.3714 | 10.3714 | 10.5801 | 10.7887 | 10.9974 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061
Braemar | 9.4367 | 9.4367 | 9.4367 | 9.2705 | 9.1042 | 8.938 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718
Braemar 2 | 9.4367 | 9.4367 | 9.4367 | 9.2705 | 9.1042 | 8.938 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718
Colongra | 10.3851 | 10.3851 | 10.3851 | 10.1781 | 9.9711 | 9.764 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557
Condamine | 9.4367 | 9.4367 | 9.4367 | 9.2705 | 9.1042 | 8.938 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718
Darling Downs | 10.0682 | 10.0682 | 10.0682 | 9.4809 | 8.8935 | 8.3062 | 7.7189 | 7.7189 | 7.7189 | 7.7189 | 7.7189 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718
Dry Creek | 11.0329 | 11.0329 | 11.0329 | 10.6468 | 10.2607 | 9.8747 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886
Hallett | 10.0416 | 10.0416 | 10.0416 | 9.9111 | 9.7807 | 9.6502 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197
Jeeralang | 11.0653 | 11.5839 | 11.0653 | 10.7872 | 10.5092 | 10.2311 | 9.953 | 9.953 | 9.953 | 9.953 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355
Ladbroke Grove | 9.922 | 9.922 | 9.922 | 9.5547 | 9.1874 | 8.8201 | 8.4528 | 8.453 | 8.4533 | 8.4533 | 8.453 | 9.5062 | 9.5062 | 9.5061 | 9.5061 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506
Laverton North | 10.8976 | 11.4162 | 10.8976 | 10.661 | 10.4244 | 10.1878 | 9.9512 | 9.9512 | 9.9513 | 9.9512 | 10.0337 | 10.0337 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338
Mintaro | 11.0607 | 11.0607 | 11.0607 | 10.6755 | 10.2902 | 9.905 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197 | 9.5197
Mortlake OCGT | 11.2515 | 11.7701 | 11.2515 | 10.893 | 10.5346 | 10.1761 | 9.8176 | 9.8176 | 9.8176 | 9.8176 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001 | 9.9001
Newport | 11.063 | 11.5816 | 11.063 | 10.7851 | 10.5071 | 10.2292 | 9.9512 | 9.9512 | 9.9513 | 9.9512 | 10.0337 | 10.0337 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338
NSW CCGT | 10.3806 | 10.3806 | 10.3806 | 10.3806 | 10.083 | 9.7854 | 9.4878 | 9.1902 | 9.1905 | 9.1921 | 9.1921 | 9.1915 | 9.5413 | 9.5414 | 9.5414 | 9.5414 | 9.5416 | 9.5416 | 9.5416 | 9.5416 | 9.5416 | 9.5313
NSW OCGT | 10.3806 | 10.3806 | 10.3806 | 10.3806 | 10.083 | 9.7854 | 9.4878 | 9.1902 | 9.1905 | 9.1921 | 9.1921 | 9.1915 | 9.5413 | 9.5414 | 9.5414 | 9.5414 | 9.5416 | 9.5416 | 9.5416 | 9.5416 | 9.5416 | 9.5313
Oakey | 9.999 | 9.999 | 9.999 | 9.483 | 8.967 | 8.451 | 7.935 | 7.9593 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718
Osborne | 9.922 | 9.922 | 9.922 | 9.5547 | 9.1874 | 8.8201 | 8.4528 | 8.453 | 8.4533 | 8.4533 | 8.453 | 9.5062 | 9.5062 | 9.5061 | 9.5061 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506
Pelican Point | 11.0329 | 11.0329 | 11.0329 | 10.6468 | 10.2607 | 9.8747 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886 | 9.4886
QLD CCGT | 9.702 | 9.702 | 9.702 | 9.702 | 9.2095 | 8.7171 | 8.2246 | 7.7321 | 7.7346 | 7.8158 | 7.8158 | 8.2108 | 8.4214 | 8.4214 | 8.4214 | 8.4214 | 8.4214 | 8.7058 | 8.7058 | 8.7058 | 8.7058 | 8.7058
QLD OCGT | 9.702 | 9.702 | 9.702 | 9.702 | 9.2095 | 8.7171 | 8.2246 | 7.7321 | 7.7346 | 7.8158 | 7.8158 | 8.2108 | 8.4214 | 8.4214 | 8.4214 | 8.4214 | 8.4214 | 8.7058 | 8.7058 | 8.7058 | 8.7058 | 8.7058
Quarantine | 9.922 | 9.922 | 9.922 | 9.5547 | 9.1874 | 8.8201 | 8.4528 | 8.453 | 8.4533 | 8.4533 | 8.453 | 9.5062 | 9.5062 | 9.5061 | 9.5061 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506
Roma | 9.3342 | 9.3342 | 9.3342 | 8.7469 | 8.1596 | 7.5722 | 6.9849 | 6.9849 | 6.9849 | 6.9849 | 6.9849 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378 | 8.0378
SA OCGT | 10.2933 | 10.2933 | 10.2933 | 10.2933 | 9.962 | 9.6307 | 9.2994 | 8.9681 | 8.9736 | 9.1544 | 9.1543 | 9.1542 | 9.5053 | 9.5053 | 9.5053 | 9.5053 | 9.5052 | 9.5052 | 9.5052 | 9.5052 | 9.5052 | 9.5052
Smithfield | 10.3806 | 10.3806 | 10.3806 | 10.083 | 9.7854 | 9.4878 | 9.1902 | 9.1905 | 9.1921 | 9.1921 | 9.1915 | 9.5413 | 9.5414 | 9.5414 | 9.5414 | 9.5416 | 9.5416 | 9.5416 | 9.5416 | 9.5416 | 9.5313 | 9.5313
Somerton | 10.89 | 11.4085 | 10.89 | 10.4461 | 10.0022 | 9.5583 | 9.1144 | 9.1387 | 9.9513 | 9.9512 | 10.0337 | 10.0337 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338 | 10.0338
Swanbank E | 9.3342 | 9.3342 | 9.3342 | 9.1936 | 9.053 | 8.9124 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718 | 8.7718
Tallawarra | 10.3851 | 10.3851 | 10.3851 | 10.1781 | 9.9711 | 9.764 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557 | 9.557
Tamar Valley | 10.3714 | 10.3714 | 10.3714 | 10.5801 | 10.7887 | 10.9974 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061
TAS CCGT | 10.3714 | 10.3714 | 10.3714 | 10.3714 | 10.5801 | 10.7887 | 10.9974 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061
TAS OCGT | 10.3714 | 10.3714 | 10.3714 | 10.3714 | 10.5801 | 10.7887 | 10.9974 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061 | 11.2061
Torrens Island | 9.8528 | 9.8528 | 9.8528 | 9.5569 | 9.2609 | 8.9649 | 8.669 | 8.6934 | 9.5063 | 9.5062 | 9.5059 | 9.5062 | 9.5062 | 9.5061 | 9.5061 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506 | 9.506
Townsville | 10.3555 | 10.3555 | 10.3555 | 9.2321 | 8.1087 | 6.9852 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 5.8618 | 8.7058 | 8.7058 | 8.7058 | 8.7058 | 8.7058 | 8.7058
Uranquinty | 10.3714 | 10.3714 | 10.3714 | 9.8927 | 9.414 | 8.9353 | 8.4566 | 8.4575 | 8.4624 | 8.4622 | 8.4606 | 9.5099 | 9.5101 | 9.5102 | 9.5103 | 9.5107 | 9.5107 | 9.5107 | 9.5107 | 9.5107 | 9.4798 | 9.4798
Valley Power | 10.8999 | 11.4185 | 10.8999 | 10.6632 | 10.4265 | 10.1897 | 9.953 | 9.953 | 9.953 | 9.953 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355 | 10.0355
VIC CCGT | 10.4855 | 11.0041 | 11.5226 | 11.0041 | 10.7108 | 10.4174 | 10.1241 | 9.8308 | 9.8339 | 9.9354 | 9.9354 | 10.0179 | 10.0179 | 10.018 | 10.0179 | 10.0179 | 10.018 | 10.018 | 10.018 | 10.018 | 10.018 | 10.018
VIC OCGT | 10.4855 | 11.0041 | 11.5226 | 11.0041 | 10.7108 | 10.4174 | 10.1241 | 9.8308 | 9.8339 | 9.9354 | 9.9354 | 10.0179 | 10.0179 | 10.018 | 10.0179 | 10.0179 | 10.018 | 10.018 | 10.018 | 10.018 | 10.018 | 10.018
Yarwun | 9.5672 | 9.5672 | 9.5672 | 8.4437 | 7.3203 | 6.1969 | 5.0735 | 5.0735 | 5.0735 | 5.0735 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231 | 9.0231
High
Generator | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bairnsdale | 12.0101 | 12.0101 | 12.0101 | 13.1405 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
Barcaldine | 9.9462 | 9.9462 | 9.9462 | 11.45 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389 | 11.1389
Barker Inlet | 14.551 | 14.551 | 14.551 | 14.551 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363
Bell Bay Three | 13.908 | 13.908 | 13.908 | 15.0385 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236
Braemar | 10.4544 | 10.4544 | 10.4544 | 11.5848 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
Braemar 2 | 10.4544 | 10.4544 | 10.4544 | 11.5848 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
Colongra | 11.4189 | 11.4189 | 11.4189 | 12.5494 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071
Condamine | 10.4544 | 10.4544 | 10.4544 | 11.5848 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
Darling Downs | 10.4544 | 10.4544 | 10.4544 | 11.5848 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
Dry Creek | 11.6471 | 11.6471 | 11.6471 | 12.7775 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249
Hallett | 11.4396 | 11.4396 | 11.4396 | 12.5701 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175
Jeeralang | 12.0101 | 12.0101 | 12.0101 | 13.1405 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
Ladbroke Grove | 11.5433 | 11.5226 | 11.5433 | 12.6738 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108
Laverton North | 12.0101 | 12.0101 | 12.0101 | 13.1405 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
Mintaro | 11.4396 | 11.4396 | 11.4396 | 12.5701 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175 | 12.2175
Mortlake OCGT | 11.8234 | 11.8234 | 11.8234 | 12.9539 | 12.6012 | 12.6012 | 12.7153 | 12.7153 | 12.7153 | 12.7153 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398
Newport | 12.0101 | 12.0101 | 12.0101 | 13.1405 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
NSW CCGT | 9.3446 | 9.3446 | 9.355 | 9.4172 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573
NSW OCGT | 11.6885 | 11.6782 | 11.6885 | 11.7715 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819 | 12.819
Oakey | 10.081 | 10.081 | 10.081 | 11.5848 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
Osborne | 11.5433 | 11.5226 | 11.5433 | 12.6738 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108
Pelican Point | 11.6471 | 11.6471 | 11.6471 | 12.7775 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249 | 12.4249
QLD CCGT | 9.0024 | 10.2988 | 10.4544 | 10.4544 | 10.4544 | 10.4544 | 10.4544 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
QLD OCGT | 11.2426 | 12.8916 | 13.0783 | 13.0783 | 13.0783 | 13.0783 | 13.0783 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947 | 14.0947
Quarantine | 11.5433 | 11.5226 | 11.5433 | 12.6738 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108
Roma | 9.0438 | 9.0438 | 9.0438 | 10.5477 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573 | 10.2573
SA OCGT | 14.551 | 14.551 | 14.551 | 14.551 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363 | 15.5363
Smithfield | 14.271 | 14.271 | 14.271 | 14.271 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563 | 15.2563
Somerton | 11.9167 | 11.9167 | 11.9167 | 11.9167 | 11.9375 | 12.0101 | 13.1405 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
Swanbank E | 10.6825 | 10.6825 | 10.4544 | 10.4544 | 10.4544 | 10.4544 | 11.5848 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633 | 11.2633
Tallawarra | 9.1268 | 11.6678 | 11.4189 | 11.4189 | 11.4189 | 11.4189 | 12.5494 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071 | 12.2071
Tamar Valley | 10.361 | 14.2088 | 13.908 | 13.908 | 13.908 | 13.908 | 15.0385 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236
TAS CCGT | 10.361 | 10.1951 | 13.908 | 13.908 | 13.908 | 13.908 | 13.908 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236 | 14.6236
TAS OCGT | 12.9435 | 12.7361 | 17.3928 | 17.3928 | 17.3928 | 17.3928 | 17.3928 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744 | 18.2744
Torrens Island | 9.9565 | 11.7508 | 11.5122 | 11.4915 | 11.5122 | 11.5848 | 12.6738 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108 | 12.3108
Townsville | 8.7949 | 8.6497 | 8.463 | 8.463 | 8.463 | 8.463 | 8.463 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349 | 8.2349
Uranquinty | 10.1743 | 11.5641 | 11.3152 | 11.3152 | 11.3152 | 11.3255 | 12.4871 | 12.1656 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176 | 12.176
Valley Power | 9.718 | 12.2693 | 12.0101 | 12.0101 | 12.0101 | 12.0101 | 13.1405 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
VIC CCGT | 12.0101 | 12.0101 | 12.0101 | 12.0101 | 12.7775 | 12.7775 | 12.7775 | 12.8916 | 12.8916 | 12.8916 | 12.8916 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161 | 13.0161
VIC OCGT | 15.0074 | 15.0074 | 15.0074 | 15.0074 | 15.9719 | 15.9719 | 15.9719 | 16.1171 | 16.1171 | 16.1171 | 16.1171 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623 | 16.2623
Yarwun | 6.4199 | 6.3162 | 6.1813 | 6.1813 | 6.1813 | 6.1813 | 6.1813 | 6.005 | 6.005 | 6.005 | 6.005 | 6.005 | 6.005 | 11.6471 | 11.6471 | 11.6471 | 11.6471 | 11.6471 | 11.6471 | 11.6471 | 11.6471 | 11.6471
Low
Generator | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Bairnsdale | 8.9609 | 8.4942 | 8.8986 | 8.4942 | 8.5668 | 8.6394 | 8.7223 | 8.8157 | 8.7846 | 8.0378 | 8.0378 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
Barcaldine | 8.6808 | 7.8304 | 7.8304 | 7.8304 | 7.7889 | 7.7578 | 7.7163 | 7.6645 | 7.6437 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903 | 6.9903
Barker Inlet | 8.5045 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748
Bell Bay Three | 8.9505 | 8.0793 | 8.0793 | 8.0793 | 8.4942 | 8.9401 | 9.4172 | 9.9254 | 9.8943 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438
Braemar | 8.1415 | 7.3533 | 7.3533 | 7.3533 | 7.4467 | 7.54 | 7.6541 | 7.7682 | 7.7474 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837
Braemar 2 | 8.1415 | 7.3533 | 7.3533 | 7.3533 | 7.4467 | 7.54 | 7.6541 | 7.7682 | 7.7474 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837
Colongra | 8.9609 | 8.0897 | 8.0897 | 8.0897 | 8.1726 | 8.266 | 8.3593 | 8.463 | 8.4423 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163
Condamine | 8.1415 | 7.3533 | 7.3533 | 7.3533 | 7.4467 | 7.54 | 7.6541 | 7.7682 | 7.7474 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837
Darling Downs | 8.6912 | 7.8408 | 7.8408 | 7.8408 | 7.6126 | 7.3741 | 7.1148 | 6.8347 | 6.814 | 6.2332 | 6.2332 | 6.2332 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837
Dry Creek | 9.5209 | 8.5979 | 8.5979 | 8.5979 | 8.546 | 8.5045 | 8.4527 | 8.4008 | 8.3801 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645
Hallett | 8.6705 | 7.82 | 7.82 | 7.82 | 7.9548 | 8.1104 | 8.266 | 8.4319 | 8.4008 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852
Jeeralang | 9.1061 | 8.6186 | 9.0231 | 8.6186 | 8.6601 | 8.712 | 8.7638 | 8.8157 | 8.7846 | 8.0378 | 8.0378 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
Ladbroke Grove | 8.5668 | 7.7267 | 7.7267 | 7.7267 | 7.6748 | 7.6126 | 7.5504 | 7.4881 | 7.4674 | 6.8244 | 6.8244 | 6.8244 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748
Laverton North | 8.9609 | 8.4838 | 8.8883 | 8.4838 | 8.5564 | 8.6394 | 8.7223 | 8.8053 | 8.7846 | 8.0378 | 8.0378 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
Mintaro | 9.552 | 8.6186 | 8.6186 | 8.6186 | 8.5771 | 8.5253 | 8.4838 | 8.4319 | 8.4008 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852 | 7.6852
Mortlake OCGT | 9.2616 | 8.7638 | 9.1683 | 8.7638 | 8.7431 | 8.7327 | 8.712 | 8.6912 | 8.6705 | 7.9237 | 7.9237 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963 | 7.9963
Newport | 9.1061 | 8.6186 | 9.0231 | 8.6186 | 8.6601 | 8.712 | 8.7534 | 8.8053 | 8.7846 | 8.0378 | 8.0378 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
NSW CCGT | 8.9609 | 8.0897 | 8.0897 | 8.0897 | 8.3386 | 8.3593 | 8.3801 | 8.4008 | 8.1104 | 7.4155 | 7.4259 | 7.4259 | 7.4259 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059
NSW OCGT | 8.9609 | 8.0897 | 8.0897 | 8.0897 | 8.3386 | 8.3593 | 8.3801 | 8.4008 | 8.1104 | 7.4155 | 7.4259 | 7.4259 | 7.4259 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059
Oakey | 8.629 | 7.7889 | 7.7889 | 7.7889 | 7.6126 | 7.4363 | 7.2392 | 7.0214 | 7.0318 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837
Osborne | 8.5668 | 7.7267 | 7.7267 | 7.7267 | 7.6748 | 7.6126 | 7.5504 | 7.4881 | 7.4674 | 6.8244 | 6.8244 | 6.8244 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748
Pelican Point | 9.5209 | 8.5979 | 8.5979 | 8.5979 | 8.546 | 8.5045 | 8.4527 | 8.4008 | 8.3801 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645 | 7.6645
QLD CCGT | 8.3697 | 7.5607 | 7.5607 | 7.5607 | 7.7889 | 7.6333 | 7.4674 | 7.2807 | 6.8244 | 6.2436 | 6.3058 | 6.3058 | 6.6273 | 6.8036 | 6.8036 | 6.8036 | 6.8036 | 6.8036 | 7.0318 | 7.0318 | 7.0318 | 7.0318
QLD OCGT | 8.3697 | 7.5607 | 7.5607 | 7.5607 | 7.7889 | 7.6333 | 7.4674 | 7.2807 | 6.8244 | 6.2436 | 6.3058 | 6.3058 | 6.6273 | 6.8036 | 6.8036 | 6.8036 | 6.8036 | 6.8036 | 7.0318 | 7.0318 | 7.0318 | 7.0318
Quarantine | 8.5668 | 7.7267 | 7.7267 | 7.7267 | 7.6748 | 7.6126 | 7.5504 | 7.4881 | 7.4674 | 6.8244 | 6.8244 | 6.8244 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748
Roma | 8.0586 | 7.2703 | 7.2703 | 7.2703 | 7.0214 | 6.7621 | 6.4821 | 6.1813 | 6.171 | 5.642 | 5.642 | 5.642 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925
SA OCGT | 8.8883 | 8.0171 | 8.0171 | 8.0171 | 8.266 | 8.2556 | 8.2452 | 8.2349 | 7.9134 | 7.2496 | 7.3948 | 7.3948 | 7.3948 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748
Smithfield | 8.9609 | 8.0897 | 8.0897 | 8.0897 | 8.3386 | 8.3593 | 8.3801 | 8.4008 | 8.1104 | 7.4155 | 7.4259 | 7.4259 | 7.4259 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059 | 7.7059
Somerton | 8.9505 | 8.4838 | 8.8883 | 8.4838 | 8.3904 | 8.2867 | 8.183 | 8.0689 | 8.0689 | 8.0378 | 8.0378 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
Swanbank E | 8.0586 | 7.2703 | 7.2703 | 7.2703 | 7.3844 | 7.4985 | 7.6333 | 7.7682 | 7.7474 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837 | 7.0837
Tallawarra | 8.9609 | 8.0897 | 8.0897 | 8.0897 | 8.1726 | 8.266 | 8.3593 | 8.463 | 8.4423 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163 | 7.7163
Tamar Valley | 8.9505 | 8.0793 | 8.0793 | 8.0793 | 8.4942 | 8.9401 | 9.4172 | 9.9254 | 9.8943 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438
TAS CCGT | 8.9505 | 8.0793 | 8.0793 | 8.0793 | 8.3282 | 8.7638 | 9.2409 | 9.7387 | 9.8943 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438
TAS OCGT | 8.9505 | 8.0793 | 8.0793 | 8.0793 | 8.3282 | 8.7638 | 9.2409 | 9.7387 | 9.8943 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438 | 9.0438
Torrens Island | 8.5045 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748
Townsville | 8.9401 | 8.0689 | 8.0689 | 8.0689 | 7.4155 | 6.7207 | 5.9843 | 5.1857 | 5.1753 | 4.7294 | 4.7294 | 4.7294 | 4.7294 | 4.7294 | 4.7294 | 4.7294 | 4.7294 | 7.0318 | 7.0318 | 7.0318 | 7.0318 | 7.0318
Uranquinty | 8.9505 | 8.0793 | 8.0793 | 8.0793 | 7.9445 | 7.7993 | 7.6541 | 7.4881 | 7.4674 | 6.8347 | 6.8347 | 6.8347 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6748 | 7.6541
Valley Power | 8.9609 | 8.4942 | 8.8986 | 8.4942 | 8.5668 | 8.6394 | 8.7223 | 8.8157 | 8.7846 | 8.0378 | 8.0378 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
VIC CCGT | 8.5979 | 8.1726 | 8.5668 | 8.9712 | 8.8364 | 8.8779 | 8.9194 | 8.9609 | 8.6808 | 7.9445 | 8.0171 | 8.0171 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897
VIC OCGT | 8.5979 | 8.1726 | 8.5668 | 8.9712 | 8.8364 | 8.8779 | 8.9194 | 8.9609 | 8.6808 | 7.9445 | 8.0171 | 8.0171 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897 | 8.0897
Yarwun | 8.2556 | 7.457 | 7.457 | 7.457 | 6.7829 | 6.0673 | 5.3101 | 4.4908 | 4.4804 | 4.0967 | 4.0967 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807 | 7.2807
$6/GJ lower bound sensitivity
Region | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
QLD | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635 | 5.9635
NSW | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925 | 6.4925
VIC | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228 | 6.2228
SA | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087 | 6.1087
TAS | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584 | 6.6584
Liquid fuel price | 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41
Liquid fuel | 36.3102 | 35.8435 | 35.2938 | 34.7441 | 34.2359 | 33.7588 | 33.3233 | 32.9395 | 32.6076 | 32.2654 | 31.9335 | 31.6223 | 31.3423 | 31.0934 | 30.8549 | 30.6267 | 30.4089 | 30.2015 | 30.0044 | 29.797 | 29.6103 | 29.2266

## Refurbishment
Refurbishment
Unit refurbishment is staggered within a power station, one unit at a time at six month intervals. In a power station with 4 units, for example, the fourth unit is not refurbished until 18 months after the given date.
Refurbishment timing
Generator | First refurbishment | Second refurbishment
Bayswater | 2025
Eraring | 2024
Mount Piper | 2023 | 2033
Vales Point | 2022
Callide B | 2028
Callide Power Plant | 2031 | 2041
Kogan Creek | 2037 | 2047
Millmerran | 2032 | 2042
Stanwell | 2026 | 2036
Tarong | 2026
Tarong North | 2033 | 2043
Loy Yang A | 2028 | 2038
Loy Yang B | 2026 | 2036
Yallourn | 2022 | 2032
Refurbishment cost
Generator class | Refurbishment cost ($/MW)1
Black coal | 158210.2467
Brown coal | 258613.5216
1. Costs are applied as an additional fixed cost for the duration of the refurbishment event.

## Retirement
Retirement
Announced and end-of-technical-life retirement. End of life retirements are determined according to equipment age. Units may be retired earlier by the model if determined as least cost to the power system.
Generator | Financial year beginning
Announced retirement
Mackay GT1 | 2021
Liddell1 | 2022
Bayswater2 | 2035
Loy Yang A2 | 2048
1. Data source: AEMO generation information page
2. Data source: AGL announcement
https://www.agl.com.au/about-agl/sustainability/rehabilitation
End of technical life
Bayswater | 2035
Eraring | 2034
Mount Piper | 2043
Vales Point | 2028
Callide B | 2038
Callide Power Plant | 2051
Gladstone | 2029
Kogan Creek | 2057
Millmerran | 2052
Stanwell | 2046
Tarong | 2036
Tarong North | 2053
Loy Yang B | 2056
Yallourn1 | 2032
Newport | 2031
Torrens Island A | 2021
1. Assumed retirement upon conclusion of current mine coal supply agreement
SA generators model can choose to retire
Torrens Island B | From 2022
Osborne | From 2022
Pelican Point | From 2022

## Heat rates
Heat rates
Encapsulates the efficiency of thermal generators (as-generated, HHV)
Existing generators |  | Generic new entrant units
Generator | Heat rate (GJ/MWh) |  | Heat rate (GJ/MWh)
Bayswater | 9.46 | OCGT | 10.15
Eraring | 9.549 | CCGT | 6.93
Liddell | 10.144 | Biomass | 12.66
Mount Piper | 9.266 | Black Coal (HELE) | 8.664
Vales Point | 9.685
Callide B | 9.149
Callide Power Plant | 9.305
Gladstone | 9.47
Kogan Creek | 8.807
Millmerran | 9.204
Stanwell | 9.073
Tarong | 9.208
Tarong North | 8.664
Loy Yang A | 12.142
Loy Yang B | 12.531
Yallourn | 13.926
Colongra | 11.139
Smithfield | 8.362
Tallawarra | 6.99
Uranquinty | 11.139
Barcaldine | 12.73
Braemar | 11.881
Condamine | 7.282
Darling Downs | 7.383
Oakey | 10.934
Roma | 11.881
Swanbank E | 7.436
Yabulu (Townsville) | 7.598
Yarwun | 10.381
Somerton | 14.851
Bairnsdale | 10.483
Jeeralang A | 15.263
Jeeralang B | 15.263
Laverton North | 11.497
Mortlake | 11.139
Newport | 10.296
Valley Power | 14.851
Hallett GT | 14.851
Barker Inlet | 7.411
Dry Creek | 13.709
Ladbroke Grove | 11.881
Mintaro | 12.73
Osborne (average) | 8.163
Osborne GT | 10.25
Osborne ST | 4.3
Pelican Point (average) | 7.353
Pelican Point GT | 8.5
Pelican Point ST | 4.3
Quarantine | 10.714
Torrens Island A | 11.429
Torrens Island B | 10.714
Bell Bay Three | 12.052
Tamar Valley CCGT | 7.282
Tamar Valley OCGT | 12.73
Hunter Valley GT | 12.73
Mackay GT | 12.73
Mount Stuart | 11.881
Angaston | 13
Lonsdale | 13
Port Lincoln | 12.821
Port Lincoln 3 | 12.821
Port Stanvac | 13
Snuggery | 13.443
Tailem Bend | 13

## Auxiliary Load
Auxiliary load
Auxiliary load is also called "parasitic load" or "self load" and refers to energy generated for use within power stations
Existing generators |  | New entrants
Generator | % Auxiliary load | Generator | % Auxiliary load
Bayswater | 6 | Wind | 1
Eraring | 6 | Solar PV | 1
Liddell | 5 | CCGT | 3
Mount Piper | 5 | OCGT | 1
Vales Point | 5 | Reciprocating engine | 3
Callide B | 9 | Biomass | 8
Callide Power Plant | 6 | Pumped Hydro | 1
Gladstone | 8 | Black Coal (HELE) | 6
Kogan Creek | 9 | Solar Thermal Central Receiver (6 hrs storage) | 1
Millmerran | 6
Stanwell | 9
Tarong | 8
Tarong North | 6
Loy Yang A | 9
Loy Yang B | 8
Yallourn | 10
Colongra | 1
Smithfield | 5
Tallawarra | 3
Uranquinty | 1
Barcaldine | 1
Braemar | 1
Condamine | 3
Darling Downs | 6
Oakey | 1
Roma | 1
Swanbank E | 3
Yabulu (Townsville) | 3
Yarwun | 2
Somerton | 1
Bairnsdale | 1
Jeeralang A | 3
Jeeralang B | 3
Laverton North | 3
Mortlake | 1
Newport | 5
Valley Power | 1
Hallett GT | 1
Dry Creek | 1
Ladbroke Grove | 1
Mintaro | 1
Osborne | 5
Pelican Point | 2
Quarantine | 5
Torrens Island A | 5
Torrens Island B | 5
Bell Bay Three | 3
Tamar Valley | 1
Hunter Valley GT | 1
Mackay GT | 1
Mount Stuart | 1
Angaston | 2.5
Lonsdale | 2.5
Port Lincoln | 8
Port Lincoln 3 | 8
Port Stanvac | 2.5
Snuggery | 3
All hydro | 1
All wind | 1
All solar | 1

## Fixed OPEX
Fixed operating cost (real 2019 dollars)
Costs that are incurred regardless of energy generated. Scaled by 2.7% from 2015 values to account for CPI increase to 2017, then used Inflation sheet.
Existing and Committed generators |  | New entrant technologies
Generator | Fixed OPEX ($/kW/year) | Generator | Fixed OPEX ($/kW/year)
Bayswater | 56.901 | Wind | 48.9529
Eraring | 56.901 | Solar PV | 31.5705
Liddell | 60.4174 | OCGT | 4.2108
Mount Piper | 56.901 | CCGT | 10.527
Vales Point | 56.901 | Pumped hydro | 5.1857
Callide B | 57.5404 | Biomass | 131.561
Callide Power Plant | 57.5404 | Solar Thermal w/ 6hr Storage | 78.4076
Gladstone | 60.4174 | Reciprocating engine | 15.6815
Kogan Creek | 58.0838 | Black Coal (HELE) | 55.7289
Millmerran | 55.7289 | Large Scale Battery Storage (2hrs storage) | 0
Stanwell | 56.901
Tarong | 57.5404
Tarong North | 55.7289
Loy Yang A | 150.9902
Loy Yang B | 119.343
Yallourn | 156.8508
Colongra | 15.131
Smithfield | 10.6556
Tallawarra | 10.6556
Uranquinty | 15.131
Barcaldine | 15.131
Braemar | 15.131
Condamine | 10.6556
Darling Downs | 10.6556
Oakey | 15.131
Roma | 15.131
Swanbank E | 10.6556
Yabulu (Townsville) | 10.6556
Yarwun | 10.6556
Somerton | 15.131
Bairnsdale | 15.131
Jeeralang A | 15.131
Jeeralang B | 15.131
Laverton North | 15.131
Mortlake | 15.131
Newport | 46.4585
Valley Power | 15.131
Hallett GT | 15.131
Dry Creek | 15.131
Ladbroke Grove | 15.131
Mintaro | 15.131
Osborne | 10.6556
Pelican Point | 10.6556
Quarantine | 15.131
Torrens Island A | 45.2864
Torrens Island B | 45.2864
Bell Bay Three | 15.131
Tamar Valley | 15.131
Hunter Valley GT | 15.131
Mackay GT | 15.131
Mount Stuart | 15.131
Angaston | 15.6851
Lonsdale | 15.131
Port Lincoln | 15.131
Port Lincoln 3 | 15.131
Port Stanvac | 15.6851
Snuggery | 15.131
All hydro | 60.4174
All wind | 46.7749
All solar | 26.6545

## Variable OPEX
Variable operating cost (real 2019 dollars)
Costs that can be expressed in terms of energy generated, not including fuel costs. Scaled by 2.7% from 2015 values to account for CPI increase to 2017, then used Inflation sheet.
Existing and Committed generators |  | New entrant technologies
Generator | Variable OPEX ($/MWh)1 | Generator | Variable OPEX ($/MWh)
Bayswater | 1.0683 | Wind | 16.3142
Eraring | 1.0683 | Solar PV | 0
Liddell | 1.0683 | OCGT | 10.527
Mount Piper | 1.0683 | CCGT | 7.3637
Vales Point | 1.0683 | Pumped hydro | 5.1857
Callide B | 1.0683 | Biomass | 8.4216
Callide Power Plant | 1.0683 | Solar Thermal w/ 6hr Storage | 6.2073
Gladstone | 1.0683 | Reciprocating engine | 11.5952
Kogan Creek | 0.52894 | Black Coal (HELE) | 1.0683
Millmerran | 3.2981 | Large Scale Battery Storage (2hrs storage) | 0
Stanwell | 3.2981
Tarong | 3.2981
Tarong North | 1.0683
Loy Yang A | 1.0683
Loy Yang B | 1.0683
Yallourn | 1.0683
Colongra | 8.8468
Smithfield | 7.457
Tallawarra | 7.457
Uranquinty | 11.087
Barcaldine | 11.087
Braemar | 11.087
Condamine | 7.457
Darling Downs | 7.457
Oakey | 11.087
Roma | 11.087
Swanbank E | 7.457
Yabulu (Townsville) | 7.457
Yarwun | 7.457
Somerton | 11.087
Bairnsdale | 11.087
Jeeralang A | 11.087
Jeeralang B | 11.087
Laverton North | 11.087
Mortlake | 11.087
Newport | 13.3169
Valley Power | 11.087
Hallett GT | 11.087
Dry Creek | 11.087
Ladbroke Grove | 11.087
Mintaro | 11.087
Osborne | 7.457
Pelican Point | 7.457
Quarantine | 11.087
Torrens Island A | 2.2402
Torrens Island B | 2.2402
Bell Bay Three | 11.087
Tamar Valley | 11.087
Hunter Valley GT | 11.087
Mackay GT | 11.087
Mount Stuart | 11.087
Angaston | 11.5952
Lonsdale | 11.5952
Port Lincoln | 11.087
Port Lincoln 3 | 11.087
Port Stanvac | 11.5952
Snuggery | 11.087
All hydro | 7.457
All wind | 10.7759
All solar | 0
1. In capacity expansion simulations, variable OPEX may be varied by a small amount ($0.01) on a unit-by-unit basis within a power station to encourage model-driven retirement to occur on a per-unit basis

## Emissions
Emissions
Existing generators |  |  |  | Generic new entrant units, committed and advanced projects
Generator | Combustion emissions (kg/MWh) | Fugitive emissions (kg/MWh) | Total emissions (kg/MWh) | Generator | Emissions (kg/MWh)
Bayswater | 865.5122 | 47.1309 | 912.6431 | Wind | 0
Eraring | 862.3464 | 47.7966 | 910.1431 | Solar PV | 0
Liddell | 930 | 50.5917 | 980.5917 | Biomass | 57.13
Mount Piper | 862.3022 | 46.2162 | 908.5184 | Barker Inlet2 | 500.46
Vales Point | 860 | 48.3051 | 908.3051 | Solar Thermal Central Receiver (6 hrs storage) | 0
Callide B | 920 | 11.3435 | 931.3435 | Pumped Hydro (6hrs storage) / Large Scale Battery Storage (2hrs storage) | 0
Callide Power Plant | 895.323 | 11.589 | 906.912 | New entrant combustion emissions3
Gladstone | 960 | 11.7614 | 971.7614 | Generator | Emissions (kg/GJ)
Kogan Creek | 820 | 11.04 | 831.04 | OCGT | 51.53
Millmerran | 830.1346 | 11.4634 | 841.598 | CCGT | 51.53
Stanwell | 860.94 | 11.25 | 872.19 | Black Coal (HELE) | 96.14
Tarong | 860.0221 | 11.4365 | 871.4586
Tarong North | 832.9647 | 10.7908 | 843.7555 | New entrant fugitive emissions
Loy Yang A | 1150 | 4.8176 | 1154.8176 | Region | Gas Emissions (kg/GJ) | Coal Emissions (kg/GJ)
Loy Yang B | 1136.0409 | 4.9805 | 1141.0214 | Qld | 7.8 | 1.25
Yallourn | 1310 | 5.5149 | 1315.5149 | NSW | 12.8 | 5
Colongra | 640 | 142.56 | 782.56 | Vic | 3.9
Smithfield | 480.9688 | 106.7707 | 587.7395 | SA | 10.4 | 2.5
Tallawarra | 358.1395 | 89.3952 | 447.5347 | Tas | 3.9
Uranquinty | 581.7116 | 142.56 | 724.2716
Barcaldine | 999.9566 | 99.2829 | 1099.2394 | Derived new entrant emissions (kg/MWh)
Braemar | 570.4776 | 92.664 | 663.1416 | New entrant | Emissions4
Condamine | 454.3237 | 56.745 | 511.0687 | Qld OCGT | 602.1995
Darling Downs | 420.2045 | 57.3809 | 477.5854 | Qld CCGT | 411.1569
Oakey | 760 | 85.2736 | 845.2736 | NSW OCGT | 652.9495
Roma | 663.8544 | 92.664 | 756.5184 | NSW CCGT | 445.8069
Swanbank E | 370 | 57.9523 | 427.9523 | Vic OCGT | 562.6145
Yabulu | 450 | 59.2122 | 509.2122 | Vic CCGT | 384.1299
Yabulu Steam Turbine | 450 | 59.2122 | 509.2122 | SA OCGT | 628.5895
Yarwun | 532.3129 | 80.9365 | 613.2494 | SA CCGT | 429.1749
Somerton | 760 | 57.915 | 817.915 | Tas OCGT | 562.6145
Bairnsdale | 524.3273 | 40.8812 | 565.2085 | Tas CCGT | 384.1299
Jeeralang A | 819.9338 | 59.4707 | 879.4045 | Qld Coal (HELE) | 843.787
Jeeralang B | 819.9338 | 59.4707 | 879.4045 | NSW Coal (HELE) | 876.277
Laverton North | 745.3812 | 44.7987 | 790.1799 | SA Coal (HELE) | 803.4127
Mortlake | 530 | 43.4362 | 573.4362
Newport | 530 | 40.0541 | 570.0541
Valley Power | 813.6315 | 57.915 | 871.5465
Hallett GT | 1020 | 154.44 | 1174.44
Dry Creek | 1200 | 142.56 | 1342.56 | 2. Based on emissions factor of gas, modelled heat rate and fugitive emissions profile of Torrens Island A
Ladbroke Grove | 530 | 123.552 | 653.552 | 3. New entrant gas units use standard emissions rate for natural gas combined with heat rates to derive emissions.
Mintaro | 820 | 132.3771 | 952.3771 | 4. Based on a new entrant with 2017 heat rate
Osborne | 460 | 84.6857 | 544.6857
Pelican Point | 397.2675 | 76.44 | 473.7075
Quarantine | 688.8094 | 111.15 | 799.9594
Torrens Island A | 590 | 118.56 | 708.56
Torrens Island B | 570 | 111.15 | 681.15
Bell Bay Three | 617.7228 | 46.9614 | 664.6841
Tamar Valley GT | 652.9757 | 49.6414 | 702.6171
Tamar Valley ST | 410.3827 | 28.3725 | 438.7552
Hunter Valley GT | 887.1814 | 45.8229 | 933.0043
Mackay GT | 1000 | 45.8229 | 1045.8229
Mount Stuart | 955.8648 | 42.768 | 998.6328
Angaston1 | 940.2 | 73.4 | 1013.6
Lonsdale1 | 1442 | 49.8 | 1491.8
Port Lincoln | 1400 | 45.8585 | 1445.8585
Port Lincoln 3 | 1400 | 45.8585 | 1445.8585
Port Stanvac1 | 1442 | 49.8 | 1491.8
Snuggery | 1400 | 48.3508 | 1448.3508
Tailem Bend | 940.2 | 73.4 | 1013.6
All hydro | 0 | 0 | 0
All wind | 0 | 0 | 0
All solar | 0 | 0 | 0
1. Not present in source material; previous (2014) value retained
No price on carbon emissions has been assumed in the modelling

## Inflation
Inflation
Annual inflation
2016-17 | 2.13%
2017-18 | 1.9%
2018-19 | 1.78%
Future years | 2.45%

## Rooftop PV
Installed capacity - rooftop PV (MW)
Central and high scenarios | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
NSW | 1783.6581 | 2143.9152 | 2539.8994 | 2963.716 | 3394.6369 | 3814.2997 | 4248.6635 | 4683.9988 | 5093.4217 | 5499.4216 | 5949 | 6336.6393 | 6733.3308 | 7078.4224 | 7459.2903 | 7785.3549 | 8054.7383 | 8322.6125 | 8605.061 | 8855.8801 | 9064.6033 | 9283.142 | 9484.0199
QLD | 2350.0679 | 2612.7279 | 2906.2298 | 3202.4062 | 3497.836 | 3765.2925 | 4039.2225 | 4287.8204 | 4530.3411 | 4772.9576 | 5039.3042 | 5260.5353 | 5478.7588 | 5689.6449 | 5902.9357 | 6083.7458 | 6227.9152 | 6373.7361 | 6513.4022 | 6607.2377 | 6695.0813 | 6789.8581 | 6871.4443
SA | 934.2731 | 1011.8974 | 1094.2562 | 1184.2461 | 1277.0573 | 1368.4897 | 1462.0875 | 1555.8645 | 1641.4588 | 1733.1904 | 1836.5513 | 1928.7363 | 2020.4747 | 2103.5989 | 2196.714 | 2283.1133 | 2363.5435 | 2437.0435 | 2515.0621 | 2578.7076 | 2645.0384 | 2713.7257 | 2775.4809
TAS | 120.9619 | 140.1003 | 159.0575 | 178.2486 | 195.7521 | 208.3315 | 216.0986 | 221.1901 | 223.2395 | 225.6453 | 229.6787 | 232.6001 | 234.5747 | 236.1354 | 238.754 | 241.645 | 244.151 | 246.2088 | 249.5186 | 251.6287 | 253.4656 | 256.4164 | 259.1527
VIC | 1313.9453 | 1550.8982 | 1800.0946 | 2049.8255 | 2293.5444 | 2528.6804 | 2759.0282 | 2990.5114 | 3193.4814 | 3394.5882 | 3607.1836 | 3781.2846 | 3933.8507 | 4079.0616 | 4224.296 | 4357.8906 | 4479.0785 | 4585.3575 | 4691.6406 | 4774.462 | 4853.4482 | 4944.3834 | 5023.5656
Low scenario | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040
NSW | 1783.6581 | 1955.1708 | 2257.7418 | 2545.2749 | 2841.738 | 3144.0231 | 3475.3418 | 3804.1186 | 4175.7712 | 4597.6244 | 5111.7139 | 5683.198 | 6378.835 | 7162.8412 | 8016.4461 | 8773.9474 | 9454.0315 | 9998.0636 | 10451.3507 | 10752.6742 | 11046.1993 | 11292.5593 | 11550.616
QLD | 2342.4908 | 2342.4908 | 2536.9757 | 2724.4276 | 2928.3891 | 3143.3022 | 3387.7569 | 3638.5787 | 3952.5533 | 4347.9505 | 4872.0521 | 5488.7913 | 6236.8321 | 7027.8516 | 7784.9394 | 8353.1999 | 8797.6179 | 9148.2209 | 9472.3807 | 9672.2479 | 9870.512 | 10048.7266 | 10251.0552
SA | 678.4079 | 1055.7449 | 1155.9048 | 1246.1245 | 1342.5162 | 1445.8786 | 1565.8411 | 1683.8164 | 1806.3723 | 1912.6043 | 2003.6858 | 2061.9094 | 2116.583 | 2164.0056 | 2215.4508 | 2248.8836 | 2289.6568 | 2328.5433 | 2374.5737 | 2401.2894 | 2435.3286 | 2467.905 | 2508.431
TAS | 120.9619 | 143.0394 | 166.3129 | 189.0789 | 213.6218 | 238.5496 | 265.0951 | 290.1263 | 317.4272 | 345.3966 | 376.1682 | 405.0717 | 438.3612 | 475.4929 | 520.2404 | 566.2657 | 620.8337 | 679.785 | 743.6927 | 797.696 | 848.0449 | 889.4481 | 926.3421
VIC | 1313.9453 | 1521.7636 | 1789.5825 | 2054.14 | 2339.9299 | 2641.2489 | 2980.6397 | 3325.0443 | 3719.6235 | 4172.1374 | 4731.2109 | 5369.7689 | 6184.7475 | 7169.4214 | 8327.9884 | 9471.5427 | 10593.8116 | 11549.5116 | 12346.7941 | 12842.4191 | 13286.5773 | 13672.5229 | 14058.2448